Copyright 2018 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to Activar Construction Products Group, Inc. - JL Industries ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Activar Construction Products Group, Inc. - JL Industries, 9702 Newton Ave. S., Bloomington, MN 55431; Phone (800) 554-6077; Website: www.activarcpg.com; Email: sales@activarcpg.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 104416 - FIRE EXTINGUISHERS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

GENERAL

SUMMARY

Section includes portable, [hand-carried] [wheeled] fire extinguishers[ and mounting brackets for fire extinguishers].

Owner-Furnished Material: [Hand-carried] [Wheeled] fire extinguishers.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 104413 "Fire Protection Cabinets."

Section 233813 "Commercial-Kitchen Hoods" for fire-extinguishing systems provided as part of commercial-kitchen exhaust hoods.

ALLOWANCES

Retain products and Work included in this Section that are covered by cash or quantity allowance. Do not include amounts. Insert descriptions of items in Part 2 or 3 to provide information affecting the cost of the Work that is not included under the allowance.

Fire Extinguishers are part of <Insert name of allowance>.

UNIT PRICES

Retain this article if Work specified in this Section is measured and paid for under the provisions of unit prices. Do not include amounts. Insert descriptions of items in Part 2 or 3 to provide information affecting the cost of the Work that is not included under the unit price.

Work of this Section is affected by <Insert name of unit price>.

PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a preinstallation conference.

Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

Retain subparagraph below if additional requirements are necessary; include information about conference.

Review methods and procedures related to fire extinguishers including, but not limited to, the following:

Schedules and coordination requirements.

ACTION SUBMITTALS

Product Data: For each type of product. Include rating and classification, material descriptions, dimensions of individual components and profiles, and finishes for fire extinguisher[ and mounting brackets].

Product Schedule: For fire extinguishers. Coordinate final fire-extinguisher schedule with fire-protection cabinet schedule to ensure proper fit and function.[ Use same designations indicated on Drawings.]

INFORMATIONAL SUBMITTALS

Warranty: Sample of special warranty.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For fire extinguishers to include in maintenance manuals.

COORDINATION

Consider retaining this article if fire-protection cabinets are specified by series only or for complex projects.

Coordinate type and capacity of fire extinguishers with fire-protection cabinets to ensure fit and function.

WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace fire extinguishers that fail in materials or workmanship within specified warranty period.

Failures include, but are not limited to, the following:

Hydrostatic test in first subparagraph below is required every five years for water, AFFF, FFFP, dry-chemical-in-stainless steel-shell, carbon dioxide, and wet-chemical fire extinguishers; test is required every 12 years for other dry-chemical, dry-powder, and halogenated-agent fire extinguishers.

Failure of hydrostatic test in accordance with NFPA 10 when testing interval required by NFPA 10 is within the warranty period.

Faulty operation of valves or release levers.

Verify available warranties and warranty periods for fire extinguishers with manufacturers.

Warranty Period: [Six] <Insert number> years from date of Substantial Completion.

PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

PERFORMANCE REQUIREMENTS

NFPA Compliance: Fabricate and label fire extinguishers to comply with NFPA 10, "Portable Fire Extinguishers."

Fire Extinguishers: Listed and labeled for type, rating, and classification by an independent testing agency acceptable to authorities having jurisdiction.

Retain subparagraph below if required for insurance purposes; verify availability with manufacturers because not all products comply.

Provide fire extinguishers approved, listed, and labeled by FM Global.

PORTABLE, HAND-CARRIED FIRE EXTINGUISHERS

See the tables at the end of the Evaluations for a list of manufacturers' products. Use these tables in combination with manufacturers' catalogs or product data to insert series, type, model, and designations of other characteristics.

Fire Extinguishers: Type, size, and capacity for each [fire-protection cabinet] [and] [mounting bracket] indicated.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries Basis-of-Design product indicated or comparable product by one of the following:

Amerex Corporation.

Ansul by Johnson Controls Company.

Buckeye Fire Equipment Company.

<Insert manufacturer's name>.

Retain "Source Limitations" Paragraph below if requiring fire extinguishers and fire-protection cabinets to be from same manufacturer. Verify availability with manufacturers.

Source Limitations: Obtain fire extinguishers, fire-protection cabinets, and accessories, from single source from single manufacturer.

Instruction Labels: Include pictorial marking system complying with NFPA 10, Appendix B[, and bar coding for documenting fire-extinguisher location, inspections, maintenance, and recharging].

In remaining paragraphs, the letter A, B, C, D, or K indicates the class of fire on which an extinguisher is effective. Class A and Class B are preceded by a rating numeral indicating the extinguisher's relative extinguishing effectiveness. Extinguishers for Class C, Class D, and Class K fires are not required to have a rating numeral. See the Evaluations for fire classifications and numerical rating explanation.

In retained paragraphs below, insert drawing designation. Use these designations on Drawings to identify each product.

Retain one or more of first three paragraphs below for stored-pressure water-type extinguishers. Potential for freezing exists with all types. Retain second paragraph if freeze potential is high.

Stored-Pressure Water Type <Insert drawing designation>: UL-rated 2-A, 2.5-gal. (9.5-L) nominal capacity, with water in stainless steel container; with pressure-indicating gauge.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; Grenadier P, Model FP02 or comparable product.

Stored-Pressure Water-Mist Type <Insert drawing designation>: UL-rated 2-A:C, [1.6-gal. (6-L)] [2.5-gal. (9.5-L)] nominal capacity, with water in enameled-steel container; with pressure-indicating gauge.

Visit http://www.activarcpg.com/jl-industries/fire-extinguishers for additional product information.

- JL Industries "Nebula" extinguisher models below compatible with non-magnetic bracket model "MN81NM."

Retain first below for 1.6-gallon model; retain second option for 2.5-gallon model.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; Nebula extinguisher Model [FE270] [FE272] or comparable product.

Wet-Chemical Type <Insert drawing designation>: UL-rated 2-A:K, 1-A:K, [1.8-gal. (6.8-L)] [2.5-gal. (9.5-L)] nominal capacity, with potassium acetate-based chemical in stainless steel container; with pressure-indicating gauge.

- JL Industries "Saturn" extinguisher models below compatible with bracket model "MB810C."

Visit http://www.activarcpg.com/jl-industries/fire-extinguishers for additional product information.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product or a comparable product.

Retain first option below for 1.8-gallon model; retain second option for 2.5-gallon model.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; Saturn extinguisher Model [FK15C] [FK25C] or comparable product.

Regular Dry-Chemical Type <Insert drawing designation>: UL-rated <Insert capacity> nominal capacity, with sodium bicarbonate-based dry chemical in manufacturer's standard enameled container.

- JL Industries "Galaxy" extinguisher models below compatible with bracket models "MB817C", "MB818C," "MB808A," "MB846C," or "MB810C."

Visit http://www.activarcpg.com/jl-industries/fire-extinguishers for additional product information.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product or a comparable product.

          - Basis-of-Design Product: provide Activar Construction Products Group, Inc. - JL Industries; "Galaxy" extinguisher Model [FG02C] [FG05C] [FG055C] [FG06C] [FG10C] [FG20C] or comparable product.

          - Valves: Manufacturer's standard.

Handles and Levers: Manufacturer's standard.

Coordinate extinguisher capacity in "Regular Dry-Chemical Type" Subparagraph below with "Basis-of-Design Product" Subparagraph selection.

Regular Dry-Chemical Type in Steel Container <Insert drawing designation>: UL-rated  [10-B:C, 2.5-lb (1.1-kg)] [10-B:C, 5-lb (2.3-kg)] [40-B:C, 5.5-lb (2.5-kg)] [40-B:C, 6-lb (2.7-kg)] [60-B:C, 10-lb (4.5-kg)] [120-B:C, 20-lb (9.1-kg)] nominal capacity, with siliconized sodium bicarbonate-based dry chemical in enameled-steel container.

- JL Industries "Galaxy" extinguisher models below compatible with bracket models "MB817C", "MB818C," "MB808A," "MB846C," or "MB810C."

Visit http://www.activarcpg.com/jl-industries/fire-extinguishers for additional product information.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product or a comparable product.

Basis-of-Design Product: provide Activar Construction Products Group, Inc. - JL Industries; "Galaxy" extinguisher Model [FG02C] [FG05C] [FG055C], [FG06C] [FG10C] [FG20C] or comparable product.Valves: Manufacturer's standard.

Handles and Levers: Manufacturer's standard.

Coordinate extinguisher capacity in "Multipurpose Dry-Chemical Type in Steel Container" Paragraph below with "Basis-of-Design Product" Subparagraph selection.

Multipurpose Dry-Chemical Type in Steel Container <Insert drawing designation>: UL-rated [1-A:10-B:C, 2.5-lb (1.1-kg)] [3-A:40-B:C, 5-lb (2.3-kg)] [3-A:40-B:C, 6-lb (2.7-kg)] [4-A:80-B:C, 10-lb (4.5-kg)] [10-A:120-B:C, 20-lb (9.1-kg)] nominal capacity, with monoammonium phosphate-based dry chemical in enameled-steel container.

- JL Industries "Galaxy" extinguisher models below compatible with bracket models "MB817C", "MB818C," "MB808A," "MB846C," or "MB811C."

Visit http://www.activarcpg.com/jl-industries/fire-extinguishers for additional product information.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; Cosmic extinguisher Model [FE2C] [FE5C] [FE6C] [FE10C] [FE20C] or comparable product.

Coordinate extinguisher capacity in "Purple-K Dry-Chemical Type in Steel Container" Subparagraph below with "Basis-of-Design Product" Subparagraph selection.

Purple-K Dry-Chemical Type in Steel Container <Insert drawing designation>: UL-rated [10-B:C, 2.5-lb (1.1-kg)] [20-B:C, 5-lb (2.3-kg)] [120-B:C, 20-lb (9.1-kg)] nominal capacity, with potassium bicarbonate-based dry chemical in steel container.

- JL Industries "Purple-K" extinguisher models below compatible with bracket models "MN817C", "MB818C," "MB808A," "MB846C," or "MB811C."

Visit http://www.activarcpg.com/jl-industries/fire-extinguishers for additional product information.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product or a comparable product.

Retain product models ending "BV" in "Basis-of-Design" Subparagraph for brass valves; select from other models for standard aluminum valves.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; Purple-K extinguisher Model [FPK02C] [FPK05C] [FPK10C] [FPK20C] [FPK10CBV] [FPK20CBV] [FPK30CBV] or comparable product.

Coordinate extinguisher capacity in "Carbon Dioxide Type" Subparagraph with "Basis-of-Design Product" Subparagraph selection.

Carbon Dioxide Type <Insert drawing designation>: UL-rated [5-B:C, 5-lb (2.3-kg)] [10-B:C, 10-lb (4.5-kg)] [10-B:C, 15-lb (6.8-kg)] [10-B:C, 20-lb (9.1-kg)] nominal capacity, with carbon dioxide in enameled-aluminum container.

- JL Industries "Sentinel" extinguisher models below compatible with bracket models "MB809C," "MB810C," or "MB811C."

Visit http://www.activarcpg.com/jl-industries/fire-extinguishers for additional product information.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product or a comparable product.

          - Basis-of-Design Product: provide Activar Construction Products Group, Inc. - JL Industries; Sentinel extinguisher Model [FS05] [FS10C] [FS15C] [FS20C] or comparable product.

          - Valves: Manufacturer's standard.

Handles and Levers: Manufacturer's standard.

Coordinate base powder options in "Dry-Powder Type" Paragraph below with Basis-of-Design models in subparagraph below.

Dry-Powder Type <Insert drawing designation>: [FM approved, ]UL-rated Class D, 30-lb (13.6-kg) nominal capacity, with [sodium chloride] [copper]-based powder in enameled-steel container; with pressure-indicating gauge.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product or a comparable product.

Retain first option below for Class D sodium chloride; retain second option for Class D copper extinguishing agent. Coordinate with "Dry Powder Type" Paragraph description above.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; extinguisher Model [FE570A] [FD30A] or comparable product.

Coordinate extinguisher capacity in "Clean-Agent Type in Steel Container" Subparagraph below with "Basis-of-Design Product" Subparagraph selection.

"Clean-Agent Type in Steel Container" Paragraph below describes JL Industries fire extinguishers using JL Industries EPA approved "Halotron" clean agent as an alternative to halon.

JL Industries nonconductive "Halotron" is FAA approved for use in airports.

Clean-Agent Type in Steel Container <Insert drawing designation>: UL-rated [2-B:C, 2.5-lb (1.1-kg)] [5-B:C, 4.75-lb (2.2-kg)] [1-A:10-B:C, 10-lb (4.5-kg)] [2-A:10-B:C, 14-lb (6.4-kg)] nominal capacity, with HFC blend agent and inert material in enameled-steel container; with pressure-indicating gauge.

- JL Industries "Mercury" extinguisher models below compatible with bracket models "MB817C," "MB818C," or "MB810C."

Visit http://www.activarcpg.com/jl-industries/fire-extinguishers for additional product information.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product or a comparable.

          - Basis-of-Design Product: provide Activar Construction Products Group, Inc. - JL Industries; Mercury extinguisher Model [FM02C] [FM05C] [FM11C] [FM15C] or comparable product.

MOUNTING BRACKETS <Insert drawing designation>

Retain this article if mounting brackets separate from fire-protection cabinets are required.

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

Mounting Brackets: Manufacturer's standard[ galvanized] steel, designed to secure fire extinguisher to wall or structure, of sizes required for types and capacities of fire extinguishers indicated, with plated or [red] [black] baked-enamel finish.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries or comparable product by one of the following:

Amerex Corporation.

Ansul by Johnson Controls Company.

Buckeye Fire Equipment Company.

<Insert manufacturer's name>.

Retain "Source Limitations" Paragraph below if requiring mounting brackets and fire extinguishers to be from same manufacturer. Verify availability with manufacturers.

Source Limitations: Obtain mounting brackets and fire extinguishers from single source from single manufacturer.

Identification: Lettering complying with authorities having jurisdiction for letter style, size, spacing, and location. Locate as indicated by Architect.

Identify bracket-mounted fire extinguishers with the words "FIRE EXTINGUISHER" in red letter decals applied to mounting surface.

If more than one orientation is required, indicate location of each on Drawings.

Orientation: [Vertical] [Horizontal].

LOW-PROFILE FIRE EXTINGUISHERS <Insert drawing designation>

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

Low-Profile Fire Extinguishers: Type, size, and capacity for locations indicated.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Coordinate extinguisher capacity in "Basis-of-Design Product" Subparagraph with extinguisher type subparagraph selection below.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; Orbit low-profile extinguishers with integral bracket or comparable product by one of the following:

Amerex Corporation.

Buckeye Fire Equipment Company.

Oval Fire Products Corporation.

<Insert manufacturer's name>.

Retain "Source Limitations" Paragraph below if requiring low-profile fire extinguishers and fire extinguishers to be from same manufacturer. Verify availability with manufacturers.

Source Limitations: Obtain low profile fire extinguishers and fire extinguishers from single source from single manufacturer.

Retain first model in "Multipurpose Dry-Chemical Type" Paragraph below if requiring low-profile fire extinguishers and fire extinguishers to be from same manufacturer. Verify availability with manufacturers.

Multipurpose Dry-Chemical Type: Activar Construction Products Group, Inc. - JL Industries Model [FE10V] [FE10VB], UL-rated 4-A:80-B:C, 10-lb (4.5-kg) nominal capacity, with monoammonium phosphate-based dry chemical in [regulated] [stored] [direct]-pressure, enameled-[steel] [aluminum] [steel or -aluminum] container; or comparable.

Purple-K Dry-Chemical Type: Activar Construction Products Group, Inc. - JL Industries; Model FPK10VB, UL-rated 80-B:C, 10-lb (4.5-kg) nominal capacity, with potassium bicarbonate-based dry chemical in [regulated] [stored] [direct]-pressure, enameled-steel container; or comparable.

WHEELED FIRE EXTINGUISHERS <Insert drawing designation>

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

Wheeled Fire Extinguishers: Type, size, and capacity for locations indicated, complete with carriage.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Coordinate extinguisher capacity in "Basis-of-Design Product" Subparagraph with extinguisher type subparagraph selections below.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; Wheeled [Multi-Purpose] [Regular Dry Chemical] extinguishers or comparable product by one of the following:

Amerex Corporation.

Ansul by Johnson Controls Company.

Buckeye Fire Equipment Company.

<Insert manufacturer's name>.

Retain "Source Limitations" Paragraph below if requiring wheeled fire extinguishers and fire extinguishers to be from same manufacturer. Verify availability with manufacturers.

Source Limitations: Obtain wheeled fire extinguishers and fire extinguishers from single source from single manufacturer.

Carriage: Fabricated from enameled-steel pipe, complete with hanger assembly, long-range nozzle, hose, and [semipneumatic solid-rubber tires] [wide-rim wheels].

Visit http://www.activarcpg.com/jl-industries/fire-extinguishers for additional product information.

Hose: [15 ft. (4.6 m)] [50 ft. (15.2 m)] [100 ft. (30.5 m)].

In remaining paragraphs, the letter A, B, C, or D indicates the class of fire on which an extinguisher is effective. Class A and Class B are preceded by a rating numeral indicating the extinguisher's relative extinguishing effectiveness. Extinguishers for Class C and Class D fires are not required to have a rating numeral. See the Evaluations for fire classifications and numerical rating explanation.

Regular Dry-Chemical Type: Activar Construction Products Group, Inc. - JL Industries UL-rated [Model 8FW496, 160-B:C, 50-lb (23-kg)] [Model 8FW31220, 240-B:C, 150-lb (68-kg)] nominal capacity, with sodium bicarbonate-based dry chemical in [regulated] [stored] [direct]-pressure, enameled-steel container; or comparable.

Verify availability of enameled-aluminum containers in "Multipurpose Dry-Chemical Type" Paragraph below with manufacturers.

Visit http://www.activarcpg.com/jl-industries/fire-extinguishers for additional product information.

Multipurpose Dry-Chemical Type: Activar Construction Products Group, Inc. - JL Industries UL-rated [Model 8FW495, 30-A:160-B:C, 50-lb (23-kg)] [Model 8FW488A, 40-A:240-B:C, 125-lb (57-kg)] nominal capacity, with monoammonium phosphate-based dry chemical in [regulated] [stored] [direct]-pressure, enameled-[steel] [aluminum] [steel or -aluminum] container; or comparable.

EXECUTION

EXAMINATION

Examine fire extinguishers for proper charging and tagging.

Remove and replace damaged, defective, or undercharged fire extinguishers.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

General: Install fire extinguishers[ and mounting brackets] in locations indicated and in compliance with requirements of authorities having jurisdiction.

Retain "Mounting Brackets" Subparagraph below if retaining option in "General" Paragraph above. If more than one height is required, indicate locations for each height. In accordance with NFPA 10, maximum mounting height for fire extinguishers weighing 40 lb (18 kg) or less is 60 inches (1524 mm) from finished floor to top of extinguisher; for those weighing more, it is 42 inches (1067 mm) from finished floor to top of extinguisher. In rooms required to comply with ADA-ABA Guidelines, mounting height for fire extinguishers is not to exceed 48 inches (1219 mm) to the handle.

Mounting Brackets: Top of fire extinguisher to be at [42 inches (1067 mm)] <Insert dimension> above finished floor.

Mounting Brackets: Fasten mounting brackets to surfaces, square and plumb, at locations indicated.

END OF SECTION 104416