Copyright 2018 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to Activar Construction Products Group, Inc. - JL Industries ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Activar Construction Products Group, Inc. - JL Industries, 9702 Newton Ave. S., Bloomington, MN 55431; Phone: (800) 554-6077; Website: www.activarcpg.com; Email: sales@activarcpg.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 077200 - ROOF ACCESSORIES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

GENERAL

SUMMARY

Section Includes:

Roof curbs.

Equipment supports.

Roof hatches.

Heat and smoke vents.

Gravity ventilators.

Pipe and duct supports.

Pipe portals.

Preformed flashing sleeves.

Roof walkways.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 055000 "Metal Fabrications" for metal vertical ladders, ships' ladders, and stairs for access to roof hatches.

Section 055213 "Pipe and Tube Railings" for safety railing systems not attached to roof-hatch curbs.

Section 076100 "Sheet Metal Roofing" for shop- and field-formed roof curbs and snow guards for sheet metal roofing.

Section 076200 "Sheet Metal Flashing and Trim" for shop- and field-formed metal flashing, roof-drainage systems, roof expansion-joint covers, and miscellaneous sheet metal trim and accessories.

Section 077100 "Roof Specialties" for manufactured fasciae, copings, gravel stops, gutters and downspouts, and counterflashing.

Section 077129 "Manufactured Roof Expansion Joints" for manufactured roof expansion-joint covers.

Section 077253 "Snow Guards" for snow guards.

Section 086200 "Unit Skylights" for single- and double-glazed domed plastic skylights with curb frame.

Section 230548 "Vibration and Seismic Controls for HVAC" for special curbs designed to accommodate seismic and vibration controls.

Section 233423 "HVAC Power Ventilators" for power roof-mounted ventilators.

Section 237413 "Packaged, Outdoor, Central-Station Air-Handling Units" for standard curbs specified with rooftop units.

[Section 284621.11 "Addressable Fire-Alarm Systems"] [Section 28462.13 "Conventional Fire-Alarm Systems"] for interconnects to automatically operated heat and smoke vents.

COORDINATION

Coordinate layout and installation of roof accessories with [roofing membrane and base flashing and ]interfacing and adjoining construction to provide a leakproof, weathertight, secure, and noncorrosive installation.

Coordinate dimensions with rough-in information or Shop Drawings of equipment to be supported.

ACTION SUBMITTALS

Product Data: For each type of roof accessory.

Include construction details, material descriptions, dimensions of individual components and profiles, and finishes.

Retain "Shop Drawings" Paragraph below for work that involves custom fabrication or if manufacturer's Product Data are inadequate.

Shop Drawings: For roof accessories.

Include plans, elevations, keyed details, and attachments to other work. Indicate dimensions, loadings, and special conditions. Distinguish between plant- and field-assembled work.

Samples: For each exposed product and for each color and texture specified, prepared on Samples of size to adequately show color.

Retain "Delegated Design Submittal" Paragraph below if design services have been delegated to Contractor.

Delegated Design Submittal: For [roof curbs] [equipment supports] [and] [walkways] indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

Detail mounting, securing, and flashing of roof-mounted items to roof structure. Indicate coordinating requirements with roof membrane system.

Wind-Restraint Details: Detail fabrication and attachment of wind restraints. Show anchorage details and indicate quantity, diameter, and depth of penetration of anchors.

Sustainable Design Submittals:

Retain "Product Data" Subparagraph below to require minimum recycled content for LEED 2009 MR Credit 4 - "Recycled Content."

Product Data: For recycled content, indicating postconsumer and preconsumer recycled content and cost.

Environmental product declaration.

"Product Certificates" Subparagraph below applies to LEED 2009, Materials and Resources Credit 5, "Regional Materials."

Product Certificates: For regional materials, indicating location of material manufacturer and point of extraction, harvest, or recovery for each raw material. Include distance to Project and cost for each regional material.

Retain "Environmental Product Declaration (EPD)" Subparagraph below for LEED v4 "MRc Building Product Disclosure and Optimization - Environmental Product Declarations." See the Evaluations. Verify, with manufacturer, that EPDs are available for each product.

Environmental Product Declaration (EPD): For each product.

"Product Certificates" Subparagraph below applies to IgCC, which requires that a minimum of 55 percent of building materials or products be extracted, harvested, manufactured, or recovered within 500 miles (800 km) of Project. See IgCC-2012, 505.2.5.

Product Certificates: For indigenous materials, indicating location of material manufacturer and point of extraction, harvest, or recovery for each raw material. Include distance to Project, means of transportation, and cost for each indigenous material.

Retain "Environmental Product Declaration" Subparagraph below if products specified in the Section are required to have an EPD to meet the IgCC's requirement of 55 percent recycled materials.

Environmental Product Declaration: For each product.

"Product Certificates" Subparagraph below applies to ASHRAE 189.1, which requires that a minimum of 15 percent of building materials or products be extracted, harvested, manufactured, or recovered within 500 miles (800 km) of Project. See ASHRAE 189.1-2014, 9.4.1.2.

Product Certificates: For regional materials, indicating location of material manufacturer and point of extraction, harvest, or recovery for each raw material. Include distance to Project, means of transportation, and cost for each regional material.

"Environmental Product Declaration" Subparagraph below applies to ASHRAE 189.1 if products specified in the Section are used to meet the requirements of paragraph 9.4.1.4, "Multiple-Attribute Product Declaration or Certification," which requires EPDs for a minimum of 10 products.

Environmental Product Declaration: For each product.

Subparagraphs below apply to Green Globes v1.4  if products specified in the Section are used to meet the requirements of paragraph 3.5.1.2 "Path B: Prescriptive Path for Building Core and Shell" -which requires that a certain percentage of the materials used in the core and shell have EPDs, third-party certifications, and/or third-party life cycle assessments.

Environmental Product Declaration: For each product.

Third-Party Certifications: For each product.

Third-Party Certified Life Cycle Assessment: For each product.

INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements; revise to suit Project.

Coordination Drawings: Roof plans, drawn to scale, and coordinating penetrations and roof-mounted items. Indicate the following:

Size and location of roof accessories specified in this Section.

Method of attaching roof accessories to roof or building structure.

Other roof-mounted items including mechanical and electrical equipment, ductwork, piping, and conduit.

Required clearances.

Sample Warranties: For manufacturer's special warranties.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For roof accessories to include in operation and maintenance manuals.

WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

Retain "Special Warranty on Painted Finishes" Paragraph below for factory-coated metal. Delete if metal is field finished or left uncoated. Coordinate with finishes retained in Part 2.

Special Warranty on Painted Finishes: Manufacturer's standard form in which manufacturer agrees to repair finishes or replace roof accessories that show evidence of deterioration of factory-applied finishes within specified warranty period.

Fluoropolymer Finish: Deterioration includes, but is not limited to, the following:

Color fading more than 5 Delta E units when tested in accordance with ASTM D2244.

Chalking in excess of a No. 8 rating when tested in accordance with ASTM D4214.

Cracking, checking, peeling, or failure of paint to adhere to bare metal.

Verify available warranties and warranty periods for finishes with manufacturers listed in Part 2. Periods of 20 years or longer are for fluoropolymer finishes and are included with manufacturers' published data; longer periods for premium finishes may be available.

Finish Warranty Period: [20] [10] <Insert number> years from date of Substantial Completion.

PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

PERFORMANCE REQUIREMENTS

General Performance: Roof accessories shall withstand exposure to weather and resist thermally induced movement without failure, rattling, leaking, or fastener disengagement due to defective manufacture, fabrication, installation, or other defects in construction.

For sound, vibration, and seismic design for roof curbs or equipment supports, see Section 230548 "Vibration and Seismic Controls for HVAC."

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

Delegated Design: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design [roof curbs] [and] [equipment supports] to comply with wind performance requirements, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain "Wind-Restraint Performance" Paragraph with "Delegated Design Submittal" Paragraph in "Action Submittals" Article for projects requiring wind-restraint design. Units are available from certain manufacturers that meet hurricane high wind zone design requirements. Verify requirements of authorities having jurisdiction.

Wind-Restraint Performance: [As indicated on Drawings] <Insert requirements>.

ROOF CURBS

Coordinate this article with Divisions 22 and 23 to avoid specifying roof curbs in multiple Sections.

Roof Curbs: Internally reinforced roof-curb units capable of supporting superimposed live and dead loads, including equipment loads and other construction indicated on Drawings, bearing continuously on roof structure, and capable of meeting performance requirements; with welded or mechanically fastened and sealed corner joints,[ straight sides,] [ integral metal cant,] [ stepped integral metal cant raised the thickness of roof insulation,] and integrally formed deck-mounting flange at perimeter bottom.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Adaptable Air Products.

AES Industries, Inc.

Air Balance; a division of MESTEK, Inc.

Conn-Fab Sales, Inc.

Curbs Plus, Inc.

Custom Solution Roof and Metal Products.

Greenheck Fan Corporation.

KCC International Inc.

Kingspan Light + Air, North America.

Lloyd Industries, Inc.

LMCurbs.

Louvers & Dampers, Inc.; a division of Mestek, Inc.

Metallic Products Corp.

Milcor; Commercial Products Group of Hart & Cooley, Inc.

Pate Company (The).

Plenums Incorporated.

Roof Curb Systems.

Roof Products and Systems (RPS); a division of Hart & Cooley, Inc.

Roof Products, Inc.

Thybar Corporation.

Vent Products Co., Inc.

<Insert manufacturer's name>.

Size: Coordinate dimensions with roughing-in information or Shop Drawings of equipment to be supported.

Retain "Supported Load Capacity" Paragraph below if load requirements from supported equipment are not indicated on Drawings. Coordinate load requirements with items being supported by curb.

Supported Load Capacity: [Coordinate load capacity with information on Shop Drawings of equipment to be supported] <Insert load requirements>.

Retain one of three "Material" paragraphs below. If Project requires more than one material or finish, indicate locations on Drawings or copy paragraph and utilize drawing designations to describe different curb types.

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.052 inch (1.32 mm)] [0.064 inch (1.63 mm)] [0.079 inch (2.01 mm)] <Insert dimension> thick.

First option in "Finish" Subparagraph below applies only to zinc-coated (galvanized) steel sheet.

Finish: [Mill phosphatized] [Factory prime coating] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain "Color" Subparagraph below if retaining either of last two options in "Finish" Subparagraph above.

Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

Material: Aluminum sheet, [0.090 inch (2.28 mm)] [0.125 inch (3.17 mm)] <Insert dimension> thick.

Finish: [Mill] [Factory prime coating] [Clear anodic] [Color anodic] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain "Color" Subparagraph below if retaining any of last three options in "Finish" Subparagraph above.

Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] [Light bronze] [Medium bronze] [Dark bronze] <Insert color>.

Material: Stainless steel sheet, [0.0781 inch (1.983 mm)] <Insert dimension> thick.

Finish: [Manufacturer's standard] [ASTM A480/A480M, No. 2D, directional polish finish] <Insert finish>.

Construction:

Revise subparagraphs below to suit Project and required curb configurations and curb accessories. Insert other features such as counterflashing if required.

Curb Profile: [Manufacturer's standard] [Profile as indicated on Drawings] compatible with roofing system.

On ribbed or fluted metal roofs, form deck-mounting flange at perimeter bottom to conform to roof profile.

Curb height in first subparagraph below may be determined by adding thickness of roof insulation to the minimum base flashing height recommended by roofing membrane manufacturer or established by office practice.

Fabricate curbs to minimum height of [12 inches (305 mm)] <Insert dimension> above roofing surface unless otherwise indicated.

Top Surface: Level top of curb, with roof slope accommodated [by sloping deck-mounting flange] [or] [by use of leveler frame].

Sloping Roofs: Where roof slope exceeds 1:48, fabricate curb with perimeter curb height tapered to accommodate roof slope so that top surface of perimeter curb is level. Equip unit with water diverter or cricket on side that obstructs water flow.

Retain "Insulation" Subparagraph below if roof curbs are required to maintain the thermal continuity of low-slope roofing membrane installation. Edit optional insulation thickness if other thickness is required for Project. Material and thickness below are standard; confirm availability of other materials and thicknesses with listed manufacturers.

Insulation: Factory insulated with [1-1/2-inch- (38-mm-)] <Insert dimension> thick glass-fiber board insulation.

Retain "Liner" Subparagraph below if interior metal liner is required for factory-insulated roof curbs.

Liner: Same material as curb, of manufacturer's standard thickness and finish.

Retain "Nailer" Subparagraph below if roofing membrane termination requires use of wood nailer.

Nailer: Factory-installed wood nailer [along top flange of curb] [under top flange on side of curb], continuous around curb perimeter.

Retain "Wind Restraint Straps and Base Flange Attachment" Subparagraph below if required by Project wind uplift performance requirements; consult Project structural engineer.

Wind Restraint Straps and Base Flange Attachment: Provide wind restraint straps, welded strap connectors, and base flange attachment to roof structure at perimeter of curb, of size and spacing required to meet wind uplift requirements.

Retain "Platform Cap" Subparagraph below if required by supported equipment configuration; consult Project HVAC engineer.

Platform Cap: Where portion of roof curb is not covered by equipment, provide weathertight platform cap formed from 3/4-inch- (19-mm-) thick plywood covered with metal sheet of same type, thickness, and finish as required for curb.

Metal Counterflashing: Manufacturer's standard, removable, fabricated of same metal and finish as curb.

Retain "Security Grille" Subparagraph below if required by Project security requirements and supported equipment configuration.

Security Grille: [Provide for all units] [Provide where indicated].

Retain "Damper Tray" Subparagraph if required by supported equipment configuration; consult Project HVAC engineer.

Damper Tray: Provide damper tray or shelf with opening [3 inches (76 mm)] <Insert dimension> [less than interior curb dimensions indicated] [of size indicated].

EQUIPMENT SUPPORTS

Coordinate this article with Divisions 22 and 23 to avoid specifying equipment supports in multiple Sections.

Equipment Supports: [Internally reinforced perimeter] [Rail-type] metal equipment supports capable of supporting superimposed live and dead loads between structural supports, including equipment loads and other construction indicated on Drawings, spanning between structural supports; capable of meeting performance requirements; with welded[ or mechanically fastened and sealed] corner joints,[ integral metal cant,] [ stepped integral metal cant raised the thickness of roof insulation,] and integrally formed structure-mounting flange at bottom.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Adaptable Air Products.

AES Industries, Inc.

Air Balance; a division of MESTEK, Inc.

Conn-Fab Sales, Inc.

Curbs Plus, Inc.

Custom Solution Roof and Metal Products.

Greenheck Fan Corporation.

KCC International Inc.

Lloyd Industries, Inc.

LMCurbs.

Louvers & Dampers, Inc.; a division of Mestek, Inc.

Milcor; Commercial Products Group of Hart & Cooley, Inc.

Pate Company (The).

Plenums Incorporated.

Roof Curb Systems.

Roof Products and Systems (RPS); a division of Hart & Cooley, Inc.

Roof Products, Inc.

Thybar Corporation.

Vent Products Co., Inc.

<Insert manufacturer's name>.

Size: Coordinate dimensions with roughing-in information or Shop Drawings of equipment to be supported.

Retain "Supported Load Capacity" Paragraph below if load requirements from supported equipment are not indicated on Drawings. Coordinate load requirements with items being supported by equipment supports.

Supported Load Capacity: [Coordinate load capacity with information on Shop Drawings of equipment to be supported] <Insert load requirements>.

Retain one of three "Material" paragraphs below. If Project requires more than one material or finish, indicate locations on Drawings or copy paragraph and utilize drawing designations to describe different curb types.

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.052 inch (1.32 mm)] [0.064 inch (1.63 mm)] [0.079 inch (2.01 mm)] <Insert dimension> thick.

First option in "Finish" Subparagraph below applies only to zinc-coated (galvanized) steel sheet.

Finish: [Mill phosphatized] [Factory prime coating] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain "Color" Subparagraph below if retaining either of last two options in "Finish" Subparagraph above.

Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

Material: Aluminum sheet, [0.090 inch (2.28 mm)] [0.125 inch (3.17 mm)] <Insert dimension> thick.

Finish: [Mill] [Factory prime coating] [Clear anodic] [Color anodic] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain "Color" Subparagraph below if retaining any of last three options in "Finish" Subparagraph above.

Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] [Light bronze] [Medium bronze] [Dark bronze] <Insert color>.

Material: Stainless steel sheet, [0.0781 inch (1.983 mm)] <Insert dimension> thick.

Finish: [Manufacturer's standard] [ASTM A480/A480M, No. 2D, directional polish finish] <Insert finish>.

Construction:

Revise subparagraphs below to suit Project and required equipment support configurations. Insert other features such as counterflashing if required.

Curb Profile: [Manufacturer's standard] [Profile as indicated on Drawings] compatible with roofing system.

Retain "Insulation" Subparagraph if insulated perimeter-type equipment supports are required to maintain the thermal continuity of low-slope roofing membrane installation. Edit optional insulation thickness if other thickness is required for Project. Material and thickness below are standard; confirm availability of other materials and thicknesses with listed manufacturers.

Insulation: Factory insulated with [1-1/2-inch- (38-mm-)] <Insert dimension> thick glass-fiber board insulation.

Retain "Liner" Subparagraph below if interior metal liner is required for factory-insulated equipment supports.

Liner: Same material as equipment support, of manufacturer's standard thickness and finish.

Retain "Nailer" Subparagraph if roofing membrane termination requires use of wood nailer.

Nailer: Factory-installed continuous wood nailers [3-1/2 inches (90 mm)] [5-1/2 inches (140 mm)] <Insert dimension> wide [on top flange of equipment supports] [under top flange on side of curb], continuous around support perimeter.

Retain "Wind Restraint Straps and Base Flange Attachment" Subparagraph below if required by Project wind uplift performance requirements; consult Project structural engineer.

Wind Restraint Straps and Base Flange Attachment: Provide wind restraint straps, welded strap connectors, and base flange attachment to roof structure at perimeter of curb of size and spacing required to meet wind uplift requirements.

Retain "Platform Cap" Subparagraph below if required by supported equipment configuration on perimeter-type supports; consult Project HVAC engineer.

Platform Cap: Where portion of equipment support is not covered by equipment, provide weathertight platform cap formed from 3/4-inch- (19-mm-) thick plywood covered with metal sheet of same type, thickness, and finish as required for curb.

Metal Counterflashing: Manufacturer's standard, removable, fabricated of same metal and finish as equipment support.

On ribbed or fluted metal roofs, form deck-mounting flange at perimeter bottom to conform to roof profile.

Equipment-support height in first subparagraph below may be determined by adding thickness of roof insulation to the minimum base flashing height recommended by roofing membrane manufacturer or established by office practice.

Fabricate equipment supports to minimum height of [12 inches (305 mm)] <Insert dimension> above roofing surface unless otherwise indicated.

Sloping Roofs: Where roof slope exceeds 1:48, fabricate each support with height to accommodate roof slope so that tops of supports are level with each other. Equip supports with water diverters or crickets on sides that obstruct water flow.

Retain "Security Grille" Subparagraph below if required; revise to suit Project.

Security Grille: [Provide for all units] [Provide where indicated on Drawings].

ROOF HATCHES

Roof Hatches: Metal roof-hatch units with lids and insulated [single] [double]-walled curbs, welded or mechanically fastened and sealed corner joints, continuous lid-to-curb counterflashing and weathertight perimeter gasketing, straight sides, and integrally formed deck-mounting flange at perimeter bottom.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; Basis-of-Design product indicated or comparable product by one of the following:

Acudor Products, Inc.

BILCO Company (The).

Dur-Red Products.

<Insert manufacturer's name>.

For more than one type or size, indicate locations on Drawings or by inserts. Retain "Single-Leaf Lid" Paragraph below for single-leaf roof hatch typically used for personnel and small equipment access via fixed ladder, ship's ladder, or service stair; Retain "Double-Leaf Lid" Paragraph below for double-leaf roof hatch typically used for equipment access. Options are most manufacturers' stock sizes.

Single-Leaf Lid: Activar Construction Products Group, Inc. -JL Industries; [RHDA Aluminum Diamond] [RHDG Galvannealed Steel Diamond] [RHGD Galvanized Steel with Dome] [RHG-STH Galvanized Steel with Safety Railing] Series roof hatch or comparable.

Retain "Aluminum Size" Subparagraph below with JL Industries "RHDA" model roof hatch.

Aluminum Size: [36 by 30 inches (914 by 762 mm), RHDA-1] [30 by 54 inches (762 by 1372 mm), RHDA-2] [30 by 36 inches (762 by 914 mm), RHDA-3] [36 by 36 inches (914 by 914 mm), RHDA-4] [48 by 48 inches (1219 by 1219 mm), RHDA-5] [32 by 72 inches (813 by 1829 mm), RHDA-6] [37 by 30 inches (940 by 762 mm), RHDA-7] <Insert dimensions>.

Retain "Galvannealed Steel Size" Subparagraph below with JL Industries "RHDG" model roof hatch.

Galvannealed Steel Size: [36 by 30 inches (914 by 762 mm), RHDG-1WT] [30 by 54 inches (762 by 1372 mm), RHDG-2WT] [30 by 96 inches (762 by 2438 mm), RHDG-3WT] [36 by 36 inches (914 by 914 mm), RHDG-4WT] [48 by 48 inches (1219 by 1219 mm), RHDG-5WT] [32 by 72 inches (813 by 1829 mm), RHDG-6WT] [37 by 30 inches (940 by 762 mm), RHDG-7WT] <Insert dimensions>.

Retain "Galvanized Steel - Domed Size" Subparagraph below with JL Industries "RHGD" model domed roof hatch with safety railing.

Galvanized Steel - Domed Size: [36 by 30 inches (914 by 762 mm), RHGD-1] [54 by 30 inches (1372 by 762 mm), RHGD-2] [96 by 30 inches (2438 by 762 mm), RHGD-3] [36 by 36 inches (914 by 914 mm), RHGD-4] [48 by 48 inches (1219 by 1219 mm), RHGD-5] <Insert dimensions>.

Retain "Galvanized Steel with Safety Railing Size" Subparagraph below with JL Industries "RHG-STH" model roof hatch with safety railing.

Galvanized Steel with Safety Railing Size: [30 by 30 inches (762 by 762 mm)] [36 by 30 inches (914 by 762 mm), RHG-1-STH] [36 by 36 inches (914 by 914 mm) , RHG-4-STH] [48 by 48 inches (1219 by 1219 mm), RHGD-5-STH] [54 by 30 inches (1372 by 762 mm), RHG-2-STH] [96 by 30 inches (2438 by 762 mm), RHG-3-STH] <Insert dimensions>.

Retain "Double-Leaf Lid" Paragraph below for double-leaf roof hatch typically used for equipment access.

Double-Leaf Lid: Activar Construction Products Group, Inc. - JL Industries; [DEHA] [DEHG] [EHA] [EHG] Series equipment hatch or comparable.

Retain "Aluminum Double-Leaf Size" Subparagraph below with JL Industries "EHA" model roof hatch.

Aluminum Double-Leaf Size: [72 by 96 inches (1829 by 2438 mm), EHA-1] [60 by 120 inches (1524 by 3048 mm), EHA-2] [120 by 120 inches (3048 by 3048 mm), EHA-3] [144 by 144 inches (3658 by 3658 mm), EHA-4] <Insert dimensions>.

Retain "Aluminum Double-Leaf - Domed Size" Subparagraph below with JL Industries "DEHA" model domed roof hatch.

Aluminum Double-Leaf - Domed Size: [72 by 96 inches (1829 by 2438 mm), DEHA-1] [60 by 120 inches (1524 by 3048 mm), DEHA-2] [120 by 120 inches (3048 by 3048 mm), DEHA-3] [144 by 144 inches (3658 by 3658 mm), DEHA-4] <Insert dimensions>.

Retain "Galvanized Steel Double-Leaf Size" Subparagraph below with JL Industries "EHG" model roof hatch.

Galvanized Steel Double-Leaf Size: [72 by 96 inches (1829 by 2438 mm), EHG-1] [60 by 120 inches (1524 by 3048 mm), EHGA-2] [120 by 120 inches (3048 by 3048 mm), EHGA-3] [144 by 144 inches (3658 by 3658 mm), EHGA-4] <Insert dimensions>.

Retain "Galvanized Steel Double Leaf - Domed Size" Subparagraph below with JL Industries "DEHG" model domed roof hatch.

Galvanized Steel Double-Leaf - Domed Size: [72 by 96 inches (1829 by 2438 mm), DEHG-1] [60 by 120 inches (1524 by 3048 mm), DEHGA-2] [120 by 120 inches (3048 by 3048 mm), DEHGA-3] [144 by 144 inches (3658 by 3658 mm), DEHGA-4] <Insert dimensions>.

Verify load requirements with authorities having jurisdiction.

Loads: Minimum 40-lbf/sq. ft. (1.9-kPa) <Insert value> external live load and 20-lbf/sq. ft. (0.95-kPa) <Insert value> internal uplift load.

Retain "Dome Glazing" Subparagraph below with JL Industries "DEHG," "DEHA" or "RHGD" domed roof hatches above.

Dome Glazing: Minimum 40-lbf/sq. ft. (1.9-kPa) external live load and 20-lbf/sq. ft. (0.95-kPa) internal uplift load.

Retain one of three "Hatch Material" paragraphs below. If Project requires more than one material or finish, indicate locations on Drawings or by inserts.

Retain "Hatch Material" Paragraph below with JL Industries "EHG," "DEHG," "RHDG," "RHGD," or "RHG-STH" roof hatch models.

Retain first option "Hatch Material" Paragraph below with JL Industries "RHDG" model roof hatch; second option for all other steel sheet models.

Hatch Material: [Galvannealed] [Zinc-coated (galvanized)] steel sheet.

Thickness: [0.079 inch (2.01 mm)] <Insert dimension>.

First option in "Finish" Subparagraph below applies only to zinc-coated (galvanized) steel sheet.

Finish: [Factory prime coating] [Baked enamel or powder coat].

First option in "Standard Textured Color" Subparagraph below for roof hatches; retain second option for equipment hatch.

Standard Textured Color: [White (WT)] [Silver Prime].

Additional Colors: [Gray Texture (GT)] [Red Texture (RT)] [Bronze Texture (BT)] <Insert custom color>.

Retain "Hatch Material" Paragraph below with JL Industries "EHA," "DEHA," or "RHDA" roof hatch models.

Hatch Material: Aluminum sheet.

Thickness: 0.079 inch (2.01 mm).

Retain first option in "Finish" Subparagraph below for JL Industries standard aluminum finish; retain second option as required to suit project; retain third option for upgrade to fluoropolymer.

Finish: [Mill] [Baked enamel or powder coat] [Two-coat fluoropolymer].

Retain "Powder Coat Color" Subparagraph below if with third option in "Finish" Subparagraph above.

Powder Coat Color: [White (WT)] [Gray Texture (GT)] [Red Texture (RT)] [Bronze Texture (BT)].

View JL Industries Fluoropolymer warranty, available hues, and related information by visiting http://www.activarcpg.com/sites/default/files/products/TechnicalInformation/Optional_PVDF_Finishes_For_RHDA_Roof_Hatches.pdf.

Fluoropolymer Color: [Beige] [Black] [Bone White] [Brick Red] [Burnt Sun] [Boysenberry] [Charcoal Gray] [Dark Ivy] [Dijon] [Dove Gray] [Hartford Green] [Ivory] [Patina Green] [Light Seawolf Beige] [Military Blue] [Midnight Blue] [Sage Brown] [Sandstone] [Slate Gray] [Quaker Bronze].

Construction:

Retain one material option in "Insulation" Subparagraph below; options are presented in ascending order of cost and thermal resistance; third option for high-performing insulation is available from some of the listed manufacturers.

Retain first or second option in "Insulation" Subparagraph below with JL Industries products above.

- JL Industries roof hatches feature high-performing polyisocyanurate insulation as a standard.

Insulation: [1-inch- (25-mm-) thick, polyisocyanurate board] [2-inch- (50-mm-) thick, polyisocyanurate board]. [1-inch- (25-mm-) thick, cellulosic-fiber board] [1-inch- (25-mm-) thick, glass-fiber board]

In "R-Value" Subparagraph below, first option corresponds with cellulosic-fiber board insulation, second option corresponds with glass-fiber board insulation, and third option corresponds with polyisocyanurate board insulation specified in "Insulation" Subparagraph above.

R-Value: [6] [12.0] <Insert R-value> in accordance with ASTM C1363.

Retain one of two "Hatch Lid" subparagraphs below; first is more common.

Hatch Lid: [Opaque] [Glazed], insulated, and double walled, with manufacturer's standard metal liner of same material and finish as outer metal lid.

Retain "Curb Liner" Subparagraph below if requiring a double-walled curb.

Curb Liner: Manufacturer's standard, of same material and finish as metal curb.

On ribbed or fluted metal roofs, form flange at perimeter bottom to conform to roof profile.

Curb height in first subparagraph below may be determined by adding thickness of roof insulation to the minimum base flashing height recommended by roofing membrane manufacturer or established by office practice.

Fabricate curbs to minimum height of [12 inches (305 mm)] <Insert dimension> above roofing surface unless otherwise indicated.

Sloping Roofs: Where slope or roof deck exceeds 1:48, fabricate curb with perimeter curb height that is [constant] [tapered to accommodate roof slope so that top surfaces of perimeter curb are level]. Equip hatch with water diverter or cricket on side that obstructs water flow.

Retain "Hatch-Lid Glazing" Paragraph below if hatch lid is glazed.

Hatch-Lid Glazing: [Single] [Double] [acrylic] glazing of thickness capable of resisting indicated loads.

Single-Dome Color: [Colorless, transparent] [White, translucent].

Retain "Single-Dome Color" Subparagraph above or both "Outer Double-Dome Color" and "Inner Double-Dome Color" subparagraphs below.

Outer Double-Dome Color: [Colorless, transparent] [White, translucent].

Inner Double-Dome Color: [Colorless, transparent] [White, translucent].

Galvanized-steel hardware in "Hardware" Paragraph below is standard; stainless steel may be available for corrosive environments. Keyed cylinders and high security locking are available from some manufacturers. Verify availability with manufacturers.

Hardware: Spring operators, hold-open arm, [galvanized] [stainless] steel spring latch with turn handles, [galvanized] [stainless] steel butt- or pintle-type hinge system, and padlock hasps inside and outside.

Retain one or both "Safety Railing System" and "Ladder-Assist Post" paragraphs below; revise to suit Project. If retaining both paragraphs, indicate location of each on Drawings or by inserts. Consult authorities having jurisdiction for their requirements. See the Evaluations.

Retain "Safety Railing System" Paragraph below with JL Industries "Single-Leaf Lid" roof hatch models above as required to suit project. Verify availability

Safety Railing System: Roof-hatch manufacturer's standard system including rails, clamps, fasteners, safety barrier at railing opening, and accessories required for a complete installation; attached to roof hatch and complying with 29 CFR 1910.29 requirements and authorities having jurisdiction.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; SAF-T-Hatch, SHWC rooftop safety railing or comparable product by one of the following:

Acudor Products, Inc.

BILCO Company (The).

Milcor; Commercial Products Group of Hart & Cooley, Inc.

<Insert manufacturer's name>.

JL Industries safety railing complies with OSHA CFR 29-1910.29 when ordered with self-closing rigid gate.

Retain "Height" Subparagraph below if railing system is not fully detailed on Drawings. Option is based on OSHA fall protection requirements; revise to suit Project.

Height: [42 inches (1060 mm)] <Insert dimension> above finished roof deck.

Dimensions in "Posts and Rails" and "Flat Bar" Subparagraphs below are typical; other diameters and thicknesses may be specified; revise to suit Project.

Posts and Rails: Galvanized steel tube, 1-5/8 inches (41 mm) in diameter.

Flat Bar: Galvanized steel, 2 inches (50 mm) high by 3/8 inch (9 mm) thick.

Retain "Maximum Opening Size" Subparagraph below if railing system is not fully detailed on Drawings. Requirement is based on IBC for required guards; revise to suit Project.

Maximum Opening Size: System constructed to prevent passage of a sphere 21 inches (533 mm) in diameter.

Self-Closing Rigid Gate: JL Industries "SHG" or comparable. Fabricated of same materials and rail spacing as safety railing system. Provide manufacturer's standard hinges and self-latching mechanism.

Post and Rail Tops and Ends: Weather resistant, closed or plugged with prefabricated end fittings.

Provide weep holes or another means to drain entrapped water in hollow sections of handrail and railing members.

Fabricate joints exposed to weather to be watertight.

Fasteners: Manufacturer's standard, finished to match railing system.

Finish: Manufacturer's standard.

Color: Safety Yellow.

Ladder-Assist Post: Roof-hatch manufacturer's standard device for attachment to roof-access ladder.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; model [LP-4] [LP-5] [LP-6] ladder-assist post or comparable product by one of the following:

BILCO Company (The).

Custom Solution Roof and Metal Products.

Milcor; Commercial Products Group of Hart & Cooley, Inc.

<Insert manufacturer's name>.

Operation: Post locks in place on full extension; release mechanism returns post to closed position.

Retain first option from "Operation Type" Subparagraph below with JL Industries "LP-4 and "LP-5" safety post models; retain second option with "LP-6" model.

Operation Type: [Extending] [Folding].

Option in "Height" Subparagraph below is typical height.

Height: 42 inches (1060 mm) <Insert dimension> above finished roof deck.

Material: Mild steel square tube.

Post: 1-1/2-inch- (38-mm-) tubing.

Select first option from "Finish" Paragraph below with JL Industries "LP4 and "LP-6" safety post models; second option with "LP-5" model.

Finish: [Manufacturer's standard baked enamel or powder coat] [Hot dip galvanized].

Color: Safety Yellow.

HEAT AND SMOKE VENTS

Retain "Hatch-Type Heat and Smoke Vents" Paragraph below if required for Project. Coordinate fusible link rating with rating for automated sprinkler system heads. See the Evaluations.

Hatch-Type Heat and Smoke Vents: Manufacturer's standard, with [single] [double]-walled insulated curbs, welded or mechanically fastened and sealed corner joints, integral condensation gutter, and cap flashing. Fabricate with insulated double-walled lid and continuous weathertight perimeter lid gaskets, and equip with automatic self-lifting mechanisms and UL-listed [fusible links rated at 165 deg F (74 deg C)] <Insert temperature rating> [fire-suppression system] [smoke-detection system].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

JL Industries smoke vent models "UVF-1," "UVF-2,"UVF-3" and "UVF-4" are UL Listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [UVF Smoke Vent] [UDFV Domed Smoke Vent] smoke vent or comparable product by one of the following:

BILCO Company (The).

Dur-Red Products.

Milcor; Commercial Products Group of Hart & Cooley, Inc.

<Insert manufacturer's name>.

Double-Leaf Lid: [48 by 48 inches (1219 by 1219 mm), UFV-1] [48 by 72 inches (1219 by 1828 mm), UFV-2] [48 by 90 inches (1219 by 2286 mm), UFV-3] [48 by 96 inches (1219 by 2438 mm), UFV-4] [60 by 60 inches (1524 by 1524 mm), UFV-5] [60 by 96 inches (1524 by 2438 mm), UFV-6].

Double-Leaf Lid with Dome: [48 by 48 inches (1219 by 1219 mm), UDFV-1] [48 by 72 inches (1219 by 1828 mm), UDFV-2] [48 by 90 inches (1219 by 2286 mm), UFV-3] [48 by 96 inches (1219 by 2438 mm), UDFV-4] [60 by 90 inches (1524 by 2286 mm), UDFV-5] [60 by 96 inches (1524 by 2438 mm), UDFV-6].

Verify load requirements with authorities having jurisdiction.

Loads: Minimum [40-lbf/sq. ft. (1.9-kPa)] external live load and [30-lbf/sq. ft. (1.4-kPa)] internal uplift load.

Retain first subparagraph below if required. The industry offers UL approval with values in option. If roof-load criteria are greater, consult manufacturer regarding UL approval and manual resetting requirements.

When release is actuated, lid shall open against [10-lbf/sq. ft. (0.5-kPa)] <Insert value> snow or wind load and lock in position.

Retain "Hatch-Lid Glazing" Subparagraph below if hatch lid is glazed.

Hatch-Lid Glazing: Minimum [40-lbf/sq. ft. (1.9-kPa)] external live load and [20-lbf/sq. ft. (0.95-kPa)] internal uplift load.

Revise one or more options in "Heat and Smoke Vent Standard" Subparagraph below if required by authorities having jurisdiction or for insurance purposes. Compliance with UL 793 is requirement of IBC.

Heat and Smoke Vent Standard: Provide units that have been tested and listed to comply with UL 793 .

Curb, Framing, and Lid Material: Zinc-coated (galvanized) steel sheet.

Thickness: Manufacturer's standard thickness for hatch size indicated.

First option in "Finish" Subparagraph below is standard finish. Retain second option at additional cost for color options indicated in "Color" Subparagraph below.

Color finishes are an option with for heat and smoke vent models where optional polyisocyanurate insulation is selected.

Finish: [Factory prime coating] [Baked enamel or powder coat].

Retain "Color" Subparagraph below if second option in "Finish" Subparagraph above is retained.

Color: Gray.

Construction:

Retain one material option in "Insulation" Subparagraph below; options are presented in ascending order of cost and thermal resistance; third option for high-performing insulation is available from several of the listed manufacturers.

Retain second or third option from "Insulation" Subparagraph below if second option in "Finish" Subparagraph above is retained.

Insulation: [1-inch- (25-mm-) thick, cellulosic-fiber board] [1-inch- (25-mm-) thick, polyisocyanurate board] [2-inch- (50-mm-) thick, polyisocyanurate board].

In "R-Value" Subparagraph below, first option corresponds with cellulosic-fiber board insulation, second option corresponds with glass-fiber board insulation, and third option corresponds with polyisocyanurate board insulation specified in "Insulation" Subparagraph above.

R-Value: [2.78] [4.3] [12.0] <Insert R-value> in accordance with ASTM C1363.

Retain one of two "Hatch Lid" subparagraphs below; first is more common.

Hatch Lid: Opaque, insulated, and double walled, with manufacturer's standard metal liner of same material and finish as outer metal lid.

Hatch Lid: Glazed, insulated, and double walled, with manufacturer's standard metal liner of same material and finish as outer metal lid.

Retain "Exterior Curb Liner" Subparagraph below if requiring a double-walled curb.

Exterior Curb Liner: Manufacturer's standard, of same material and finish as metal curb.

Curb height in first subparagraph below may be determined by adding thickness of roof insulation to the minimum base flashing height recommended by roofing membrane manufacturer or established by office practice.

Fabricate curbs to minimum height of [12 inches (305 mm)] <Insert dimension> above roofing surface unless otherwise indicated.

Sloping Roofs: Where slope or roof deck exceeds 1:48, fabricate curb with perimeter curb height that is [constant] [tapered to accommodate roof slope so that top surfaces of perimeter curb are level]. Equip hatch with water diverter or cricket on side that obstructs water flow.

Retain "Security Grille" Subparagraph below if required; revise to suit Project.

Security Grille: [Provide for all units] [Provide where indicated on Drawings].

Retain "Hatch-Lid Glazing" Subparagraph below if required for Project.

Hatch-Lid Glazing: Double acrylic glazing of thickness capable of resisting indicated loads; [colorless, transparent] [white, translucent].

Hardware: Manufacturer's standard; with hinges, hold-open devices, and independent manual-release devices for [inside] [and] [outside] operation of lids.

Retain "Dropout-Type Heat and Smoke Vents" Paragraph below for dropout-type heat and smoke vents. See the Evaluations.

Dropout-Type Heat and Smoke Vents: Manufacturer's standard, gravity operated and automatic; with [single] [double]-walled insulated curbs and frame, welded or mechanically fastened and sealed corner joints, integral condensation gutter, cap flashing, and heat-sensitive dome glazing that will deform and drop out of vent opening in accordance with heat and smoke vent standard indicated.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

APC Dayliter; C/S Group.

Construction Specialties, Inc.

Kingspan Light + Air, North America.

Pate Company (The).

Plasteco, Inc.

<Insert manufacturer's name>.

Size: [As indicated on Drawings] [48 by 48 inches (1219 by 1219 mm)] [48 by 60 inches (1219 by 1524 mm)] [48 by 72 inches (1219 by 1829 mm)] [48 by 90 inches (1219 by 2286 mm)] [48 by 96 inches (1219 by 2438 mm)] <Insert dimensions>.

Verify load requirements with authorities having jurisdiction.

Loads: Minimum [40-lbf/sq. ft. (1.9-kPa)] <Insert value> external live load and [30-lbf/sq. ft. (1.4-kPa)] <Insert value> internal uplift load.

Dome Glazing: Minimum [40-lbf/sq. ft. (1.9-kPa)] <Insert value> external live load and [20-lbf/sq. ft. (0.95-kPa)] <Insert value> internal uplift load.

Revise one or more options in "Heat and Smoke Vent Standard" Subparagraph below if required by authorities having jurisdiction or for insurance purposes. Compliance with UL 793 is requirement of the IBC.

Heat and Smoke Vent Standard: Provide units that have been tested and [listed to comply with UL 793] [and] [are FM Approved].

Curb and Framing Material: Aluminum sheet.

Thickness: [Manufacturer's standard thickness for vent size indicated] [0.079 inch (2.01 mm)] <Insert dimension>.

Finish: [Mill] [Factory prime coating] [Clear anodic] [Color anodic] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain "Color" Subparagraph below if retaining any of last three options in "Finish" Subparagraph above.

Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] [Light bronze] [Medium bronze] [Dark bronze] <Insert color>.

Construction:

Insulation: Manufacturer's standard.

Retain "Nailer" Subparagraph below if roofing membrane termination requires use of wood nailer.

Nailer: Factory-installed wood nailer continuous around hatch perimeter.

Retain "Exterior Curb Liner" Subparagraph below if requiring a double-walled curb.

Exterior Curb Liner: Manufacturer's standard, of same material and finish as metal curb.

Curb height in first subparagraph below may be determined by adding thickness of roof insulation to the minimum base flashing height recommended by roofing membrane manufacturer or established by office practice.

Fabricate curbs to minimum height of [12 inches (305 mm)] <Insert dimension> above roofing surface unless otherwise indicated.

Sloping Roofs: Where slope of roof deck exceeds 1:48, fabricate curb with perimeter curb height that is [constant] [tapered to accommodate roof slope so that top surfaces of perimeter curb are level]. Equip unit with water diverter or cricket on side that obstructs water flow.

Dome Glazing: [Single] [Double] [acrylic] [polycarbonate] glazing of thickness capable of resisting indicated loads.

Single-Dome Color: [Colorless, transparent] [White, translucent] [Gray tinted, transparent] [Bronze tinted, transparent] <Insert requirement>.

Retain "Dome Glazing" Subparagraph above or "Outer Double-Dome Color" and "Inner Double-Dome Color" subparagraphs below.

Outer Double-Dome Color: [Colorless, transparent] [White, translucent] [Gray tinted, transparent] [Bronze tinted, transparent] <Insert requirement>.

Inner Double-Dome Color: [Colorless, transparent] [White, translucent] [Gray tinted, transparent] [Bronze tinted, transparent] <Insert requirement>.

Fall Protection Safety Structure: Manufacturer's standard meeting impact load requirements of 29 CFR 1910.23 and authorities having jurisdiction, [equipped with hail protection galvanized steel wire mesh screen,] and manually openable from exterior without special tools.

Hardware: Manufacturer's standard, corrosion resistant; with hinges, hold-open devices, and independent manual-release devices for [inside] [and] [outside] operation of lids.

GRAVITY VENTILATORS

Coordinate with Section 233723 "HVAC Gravity Ventilators" to ensure that gravity ventilators are specified only once; gravity ventilators connected to HVAC ductwork are generally specified in Section 233723 "HVAC Gravity Ventilators." Units in this article are not ducted or dampered.

Retain one or more of three paragraphs below. Gravity ventilators are also called "static" or "relief vents" by various trades and manufacturers. The term "gravity ventilator" is used primarily by engineers. The term "static ventilator" is often used by the roofing industry. The term "relief ventilator" is often used interchangeably with the term "gravity ventilator" by manufacturers. Revise terms to suit Project. See the Evaluations.

Low-Profile, Cylindrical-Style Gravity Ventilators: Manufacturer's standard, fabricated as indicated, with manufacturer's standard welded or sealed mechanical joints.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Active Ventilation Products, Inc.

Air Vent, Inc.; a Gibraltar Industries company.

Dur-Red Products.

Greenheck Fan Corporation.

Loren Cook Company.

Metallic Products Corp.

Moffitt Corporation Inc.

PennBarry.

Romlair Ventilator Co.

Thaler Metal Industries Ltd.

Vent Products Co., Inc.

<Insert manufacturer's name>.

Construction: Integral base flange, vent cylinder, cylinder bird screen, and [rain cap] [hood].

Dimensions: [As indicated on Drawings] <Insert dimensions>.

Retain "Configuration" Subparagraph below for additional appearance and installation requirements for low-profile, cylindrical style.

Configuration: [As indicated on Drawings] <Insert requirements>.

Generally, retain either "Bird Screens" or "Insect Screens" Subparagraph below. If retaining more than one type of screen, indicate location of each on Drawings or by inserts.

Bird Screens: Manufacturer's standard mesh with rewireable frame.

Insect Screens: Manufacturer's standard mesh with rewireable frame.

Retain "Security Grille" Subparagraph below if required; revise to suit Project.

Security Grille: [Provide for all units] [Provide where indicated on Drawings].

Vent Cylinder, Base Flange, and [Rain-Cap] [Hood] Material: [Zinc-coated (galvanized) steel] [Aluminum] [Stainless steel] sheet, of manufacturer's standard thickness.

Finish: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert finish>.

Louvered Penthouse-Style Gravity Ventilators: Manufacturer's standard, fabricated as indicated, with manufacturer's standard welded or sealed mechanical joints.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Dur-Red Products.

Greenheck Fan Corporation.

Loren Cook Company.

PennBarry.

Romlair Ventilator Co.

Vent Products Co., Inc.

<Insert manufacturer's name>.

Construction: Integral frame with base flange, weathertight cap[ with clear acrylic dome] [ with white translucent acrylic dome], and weatherproof sidewall louvers.

Dimensions: [As indicated on Drawings] <Insert dimensions>.

Retain "Configuration" Subparagraph below for additional appearance and installation requirements for louvered penthouse style.

Configuration: [As indicated on Drawings] <Insert requirements>.

Generally, retain either "Bird Screens" or "Insect Screens" Subparagraph below. If retaining more than one type of screen, indicate location of each on Drawings or by inserts.

Bird Screens: Manufacturer's standard mesh with rewireable frame.

Insect Screens: Manufacturer's standard mesh with rewireable frame.

Retain "Security Grille" Subparagraph below if required; revise to suit Project.

Security Grille: [Provide for all units] [Provide where indicated on Drawings].

Frame, Base Flange, Cap, and Louver Material: [Zinc-coated (galvanized) steel] [Aluminum] [Stainless steel] sheet, of manufacturer's standard thickness.

Finish: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert finish>.

Turbine-Style Gravity Ventilators: Manufacturer's standard, fabricated as indicated, with manufacturer's standard welded or sealed mechanical joints:

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Air Vent, Inc.; a Gibraltar Industries company.

Metallic Products Corp.

Moffitt Corporation Inc.

PennBarry.

Romlair Ventilator Co.

<Insert manufacturer's name>.

Provide integral weathertight base cap, outlet duct, and rotating louvered turbine.

Throat Size and Height: [As indicated on Drawings] <Insert dimensions>.

Retain "Configuration" Subparagraph below for additional appearance and installation requirements for turbine style.

Configuration: [As indicated on Drawings] <Insert requirements>.

Generally, retain either "Bird Screen" or "Insect Screen" Subparagraph below. If retaining more than one type of screen, indicate location of each on Drawings or by inserts.

Bird Screens: Manufacturer's standard mesh with rewireable frame.

Insect Screens: Manufacturer's standard mesh with rewireable frame.

Retain "Security Grille" Subparagraph below if required; revise to suit Project.

Security Grille: [Provide for all units] [Provide where indicated on Drawings].

Air Vent makes turbine units from aluminum; Metallic Products Corp. makes units from galvanized steel.

Weathertight Base Cap, Outlet Duct, and Turbine Material: [Manufacturer's standard] [Zinc-coated (galvanized) steel] [Aluminum] sheet, of manufacturer's standard thickness.

Finish: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert finish>.

Insert other styles of gravity ventilators to suit Project.

PIPE AND DUCT SUPPORTS

Coordinate roof accessories in this article with applicable plumbing, HVAC, and electrical Sections. Pipe support assemblies vary among manufacturers. Insert descriptions of other types to suit Project.

Base, Pipe Support: UV-resistant molded recycled rubber pipe-stand base with manufacturer's support pad or deck plate as recommended for penetration-free installation over roof membrane type; as required for quantity of pipe runs and sizes.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; KeyCurb Base #RKC pipe support base or comparable product by one of the following:

Mifab.

Miro Industries.

<Insert manufacturer's name>.

Strut Type Pipe Support, Fixed Height: UV-resistant molded recycled rubber pipe-stand base with steel carrying assembly capable accommodating up to [8-inch- (203-mm-)] [12-inch- (305-mm-)] [16-inch- (406-mm-)] diameter pipe or conduit.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; KeyCurb Strut #RKCSN1 pipe support base or comparable product by one of the following:

Mifab.

Miro Industries.

<Insert manufacturer's name>.

Strut Type Pipe Support, Adjustable Height: UV-resistant molded recycled rubber pipe-stand base with steel carrying assembly capable of accommodating up to [8-inch- (203-mm-)] [12-inch- (305-mm-)] [16-inch- (406-mm-)] diameter pipe or conduit, with stainless steel threaded rod designed for adjusting support height.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; KeyCurb Strut #RKCSE1, extendable pipe support base or comparable product by one of the following:

Mifab.

Miro Industries.

<Insert manufacturer's name>.

Bridge Type Pipe Support, Fixed Height: Steel carrying assembly spanning two UV-resistant molded recycled rubber pipe-stand bases capable of accommodating up to [24-inch- (609-mm-)] [36-inch- (914-mm-)] [48-inch- (1219-mm-)] diameter pipe or conduit.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; KeyCurb Bridge Series #RKCBN2 pipe support base or comparable product by one of the following:

Mifab.

Miro Industries.

<Insert manufacturer's name>.

Bridge Type Pipe Support, Adjustable Height: Steel carrying assembly spanning two UV-resistant molded recycled rubber pipe-stand bases capable of accommodating up to [24-inch- (609-mm-)] [36-inch- (914-mm-)] [48-inch- (1219-mm-)] diameter pipe or conduit, with stainless steel threaded rod designed for adjusting support height.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; KeyCurb Bridge Series #RKCBE2, extendable pipe support base or comparable product by one of the following:

Mifab.

Miro Industries.

<Insert manufacturer's name>.

Roller Type Pipe Support, Fixed Height: UV-resistant molded recycled rubber pipe-stand base with [3-1/2 inch (88 mm)-] heavy-duty molded-plastic roller assembly capable accommodating up to [4-inch- (101-mm-)] diameter pipe or conduit.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; KeyCurb Roller Series #RKCRN1 pipe support base or comparable product by one of the following:

Mifab.

Miro Industries.

<Insert manufacturer's name>.

Roller Type Pipe Support, Adjustable Height: UV-resistant molded recycled rubber pipe-stand base with [3-1/2-inch (88-mm)-] heavy-duty molded-plastic roller assembly capable of accommodating up to [4-inch- (101-mm-)] diameter pipe or conduit, with stainless steel threaded rod designed for adjusting support height.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; KeyCurb Roller Series #RKCRE1, extendable pipe support base or comparable product by one of the following:

Mifab.

Miro Industries.

<Insert manufacturer's name>.

Duct Support, Fixed Height: Steel carrying assembly including crossbar connecting two UV-resistant molded recycled rubber pipe-stand bases capable of accommodating up to [18-inch- (609-mm-)] [24-inch- (609-mm-)] [36-inch- (914-mm-)] [48-inch- (1219-mm-)] [60-inch- (1524-mm-)] diameter pipe or conduit.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; KeyCurb Multipurpose Series #RKCMA1 pipe support base or comparable product by one of the following:

Mifab.

Miro Industries.

<Insert manufacturer's name>.

Duct Support, Adjustable Height: Steel carrying assembly with crossbar connecting spanning four UV-resistant molded recycled rubber pipe-stand bases capable of accommodating up to [18-inch- (609-mm-)] [24-inch- (609-mm-)] [36-inch- (914-mm-)] [48-inch- (1219-mm-)] [60-inch- (1524-mm-)] diameter pipe or conduit, with stainless steel threaded rod designed for adjusting support height.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; KeyCurb Multipurpose Dual Series #RKCMA2, extendable pipe support base or comparable product by one of the following:

Mifab.

Miro Industries.

<Insert manufacturer's name>.

PIPE PORTALS

Pipe portals vary among manufacturers. Paragraphs below are examples only; insert descriptions of other types to suit Project.

Curb-Mounted Pipe Portal: Insulated roof-curb units with welded or mechanically fastened and sealed corner joints,[ straight sides,] [ integral metal cant,] [ stepped integral metal cant raised the thickness of roof insulation,] and integrally formed deck-mounting flange at perimeter bottom; with weathertight curb cover with single or multiple collared openings and pressure-sealed conically shaped EPDM protective rubber caps sized for piping indicated, with stainless steel snaplock swivel clamps.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by the following:

Roof Products and Systems (RPS); a division of Hart & Cooley, Inc.

<Insert manufacturer's name>.

Flashing Pipe Portal: Formed aluminum membrane-mounting flashing flange and sleeve with collared opening and pressure-sealed conically shaped EPDM protective rubber cap sized for piping indicated, with stainless steel snaplock swivel clamps.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by the following:

Roof Products and Systems (RPS); a division of Hart & Cooley, Inc.

<Insert manufacturer's name>.

PREFORMED FLASHING SLEEVES

Preformed flashing sleeves vary among manufacturers. Paragraphs below are examples only; insert descriptions of other types to suit Project. Preformed metal flashing boots compatible with thermoplastic roofing membranes may be added here or in the corresponding roofing membrane section.

Exhaust Vent Flashing: Double-walled metal flashing sleeve or boot, insulation filled, with integral deck flange, [12 inches (300 mm)] <Insert dimension> high, with removable metal hood and [slotted] [perforated] metal collar.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Custom Solution Roof and Metal Products.

Menzies Metal Products.

Thaler Metal Industries Ltd.

<Insert manufacturer's name>.

Options in "Metal" and "Diameter" subparagraphs below are standard. Verify availability of other options with manufacturers.

Metal: Aluminum sheet, [0.063 inch (1.60 mm)] <Insert thickness> thick.

Diameter: [As indicated on Drawings] [3 inches (76 mm)] [4 inches (100 mm)] [5 inches (125 mm)] [6 inches (150 mm)] [7 inches (175 mm)] [8 inches (200 mm)] [9 inches (225 mm)] [10 inches (250 mm)] <Insert dimension>.

Finish: [Manufacturer's standard] <Insert finish>.

Vent Stack Flashing: Metal flashing sleeve, uninsulated, with integral deck flange.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Custom Solution Roof and Metal Products.

Menzies Metal Products.

Milcor; Commercial Products Group of Hart & Cooley, Inc.

Thaler Metal Industries Ltd.

<Insert manufacturer's name>.

Options in "Metal," "Height," and "Diameter" subparagraphs below are typical. Verify availability of other options with manufacturers.

Metal: [Aluminum sheet, 0.063 inch (1.60 mm) thick] <Insert material and thickness>.

Height: [7 inches (175 mm)] [13 inches (330 mm)] [19 inches (480 mm)] <Insert dimension>.

Diameter: [As indicated on Drawings] [2 inches (50 mm)] [3 inches (76 mm)] [4 inches (100 mm)] [5 inches (125 mm)] [6 inches (150 mm)] <Insert dimension>.

Finish: [Manufacturer's standard] <Insert finish>.

ROOF WALKWAYS

Retain this article for factory-fabricated roof walkways. Roof walkways can be fabricated with preservative-treated wood as specified in Section 061000 "Rough Carpentry."

"Roof Walkway" Paragraph below is an example only and describes one form of roof walkway that bears on roofing membrane; revise to suit Project. See manufacturers' catalogs for other forms of roof walkways.

Roof Walkway: Metal planking formed from multiple C-shaped channels with upper surface punched in serrated diamond or rectangular shapes to produce raised slip-resistant surface and drainage holes. Provide support framing, brackets, connectors, nosings, and other accessories and components needed for complete installation.

Include step units or stairs of similar construction for changes in elevation. Comply with ASCE-7, 29 CFR 1910.23, and requirements of authorities having jurisdiction.

Equip walkways with safety railings where required.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

B-line, an Eaton business.

MIRO Industries.

PHP Systems/Design.

Unistrut; Part of Atkore International.

<Insert manufacturer's name>.

Plank Width: [4-3/4 inches (121 mm)] [7 inches (178 mm)] [9-1/2 inches (241 mm)] [11-3/4 inches (298 mm)] [18-3/4 inches (476 mm)] [24 inches (610 mm)] [As indicated].

Walkway Width: [As indicated] <Insert dimension>.

Channel Depth: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [2-1/2 inches (64 mm)] [3 inches (76 mm)] [As indicated].

Metal Material: [0.079-inch- (2.01-mm-) thick zinc-coated (galvanized) steel sheet] [0.108-inch- (2.74-mm-) thick zinc-coated (galvanized) steel sheet] [0.0625-inch- (1.587-mm-) thick stainless steel sheet] [0.0781-inch- (1.983-mm-) thick stainless steel sheet] [0.080-inch- (2.03-mm-) thick aluminum sheet] [0.100-inch- (2.54-mm-) thick aluminum sheet] <Insert material and thickness>, perforated, with serrated slip-resistant walking surface.

Retain "Support Stands" Subparagraph below for low-slope membrane roofing and other nonmetal panel roofing. Revise to suit Project or to describe support-stand adaptors for metal panel roofing. See the Evaluations.

Support Stands: Manufacturer's standard, with protective pads compatible with roofing material.

Retain "Support Pads" Subparagraph below if required to raise support stand to match the thickness of insulation.

Support Pads: Continuous wood isolation pads, pressure-preservative treated as specified in [Section 061000 "Rough Carpentry"] [Section 061053 "Miscellaneous Rough Carpentry"]; attach roof-walkway supports to pads so that supports are separated from roof membrane surface and walkway support loads are distributed evenly.

Retain "Wind Restraint" Subparagraph below if required by Project wind uplift performance requirements.

Wind Restraint: Provide wind restraint attachment to roof structure of size and spacing required to meet wind uplift requirements.

Finish: [Manufacturer's standard] <Insert finish>.

METAL MATERIALS

Zinc-Coated (Galvanized) Steel Sheet: ASTM A653/A653M, G90 (Z275) coating designation[ and mill phosphatized for field painting where indicated].

Retain one of first four subparagraphs below. Verify, with manufacturers, the availability of finishes for products specified; revise or insert other finishes to suit Project. For field painting specified in Section 099113 "Exterior Painting" retain option in paragraph above, along with first or second subparagraph below. If retaining more than one exposed finish, indicate location of each on Drawings or by inserts.

Mill-Phosphatized Finish: Manufacturer's standard for field painting.

Factory Prime Coating: Where field painting is indicated, apply pretreatment and white or light-colored, factory-applied, baked-on epoxy primer coat, with a minimum dry film thickness of 0.2 mil (0.005 mm).

Exposed Coil-Coated Finish: Prepainted by the coil-coating process to comply with ASTM A755/A755M. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

Finish in "Two-Coat Fluoropolymer Finish" Subparagraph below is most manufacturers' standard fluoropolymer finish; three-coat fluoropolymer and other finishes may be available for custom orders. To obtain a proprietary finish system, insert names of coating manufacturers and products.

Two-Coat Fluoropolymer Finish: AAMA 621. System consisting of primer and fluoropolymer color topcoat containing not less than 70 percent polyvinylidene fluoride (PVDF) resin by weight.

Baked-Enamel or Powder-Coat Finish: After cleaning and pretreating, apply manufacturer's standard two-coat, baked-on finish consisting of prime coat and thermosetting topcoat to a minimum dry film thickness of 2 mils (0.05 mm).

Finish in "Concealed Finish" Subparagraph below is frequently retained as a factory finish for interior surfaces of coil-coated sheet. Usually, delete for other finishes.

Concealed Finish: Pretreat with manufacturer's standard white or light-colored acrylic or polyester-backer finish consisting of prime coat and wash coat, with a minimum total dry film thickness of 0.5 mil (0.013 mm).

Aluminum-Zinc Alloy-Coated Steel Sheet: ASTM A792/A792M, AZ50 (AZM150) coated.

Retain one of first three subparagraphs below. Verify, with manufacturers, the availability of finishes for products specified; revise or insert other finishes to suit Project. Retain first subparagraph for field painting specified in Section 099113 "Exterior Painting." If retaining more than one exposed finish, indicate location of each on Drawings or by inserts.

Factory Prime Coating: Where field painting is indicated, apply pretreatment and white or light-colored, factory-applied, baked-on epoxy primer coat, with a minimum dry film thickness of 0.2 mil (0.005 mm).

Exposed Coil-Coated Finish: Prepainted by the coil-coating process to comply with ASTM A755/A755M. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

Finish in "Two-Coat Fluoropolymer Finish" Subparagraph below is most manufacturers' standard fluoropolymer finish; three-coat fluoropolymer and other finishes may be available for custom orders. To obtain a proprietary finish system, insert names of coating manufacturers and products.

Two-Coat Fluoropolymer Finish: AAMA 621. System consisting of primer and fluoropolymer color topcoat containing not less than 70 percent polyvinylidene fluoride (PVDF) resin by weight.

Baked-Enamel or Powder-Coat Finish: After cleaning and pretreating, apply manufacturer's standard two-coat, baked-on finish consisting of prime coat and thermosetting topcoat to a minimum dry film thickness of 2 mils (0.05 mm).

Finish in "Concealed Finish" Subparagraph below is frequently retained as a factory finish for interior surfaces of coil-coated sheet. Usually, delete for other finishes.

Concealed Finish: Pretreat with manufacturer's standard white or light-colored acrylic or polyester-backer finish consisting of prime coat and wash coat, with a minimum total dry film thickness of 0.5 mil (0.013 mm).

Aluminum Sheet: ASTM B209 (ASTM B209M), manufacturer's standard alloy for finish required, with temper to suit forming operations and performance required.

Retain one of first six subparagraphs below. Verify, with manufacturers, the availability of finishes for products specified; revise or insert other finishes to suit Project. Retain second subparagraph for field painting specified in Section 099113 "Exterior Painting." If retaining more than one exposed finish, indicate location of each on Drawings or by inserts.

Mill Finish: As manufactured.

Factory Prime Coating: Where field painting is indicated, apply pretreatment and white or light-colored, factory-applied, baked-on epoxy primer coat, with a minimum dry film thickness of 0.2 mil (0.005 mm).

Retain one or both "Clear Anodic Finish" and "Color Anodic Finish" subparagraphs below for anodized finish; retain one of two options in either subparagraph. Class II finish is standard with many manufacturers; Class I finish is heavy anodized. Verify availability with manufacturers.

Clear Anodic Finish: AAMA 611, [AA-M12C22A41, Class I, 0.018 mm] [AA-M12C22A31, Class II, 0.010 mm] or thicker.

Color Anodic Finish: AAMA 611, [AA-M12C22A42/A44, Class I, 0.018 mm] [AA-M12C22A32/A34, Class II, 0.010 mm] or thicker.

Exposed Coil-Coated Finish: Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

Finish in "Two-Coat Fluoropolymer Finish" Subparagraph below is most manufacturers' standard fluoropolymer finish; three-coat fluoropolymer and other finishes may be available for custom orders. To obtain a proprietary finish system, insert names of coating manufacturers and products.

Two-Coat Fluoropolymer Finish: AAMA 2605. System consisting of primer and fluoropolymer color topcoat containing not less than 70 percent polyvinylidene fluoride (PVDF) resin by weight.

"Baked-Enamel or Powder-Coat Finish" Subparagraph below references AAMA standard for pigmented organic coating on extrusions and panels.

Baked-Enamel or Powder-Coat Finish: AAMA 2603 except with a minimum dry film thickness of 1.5 mils (0.04 mm). Comply with coating manufacturer's written instructions for cleaning, conversion coating, and applying and baking finish.

Finish in "Concealed Finish" Subparagraph below is frequently retained as a factory finish for interior surfaces of coil-coated sheet. Usually, delete for other finishes.

Concealed Finish: Pretreat with manufacturer's standard white or light-colored acrylic or polyester-backer finish consisting of prime coat and wash coat, with a minimum total dry film thickness of 0.5 mil (0.013 mm).

Aluminum Extrusions and Tubes: ASTM B221 (ASTM B221M), manufacturer's standard alloy and temper for type of use, finished to match assembly where used; otherwise mill finished.

Type 304 stainless steel is standard in manufacturers' literature. Revise "Stainless Steel Sheet and Shapes" Paragraph below if Type 316 stainless steel is required; verify availability with manufacturers.

Stainless Steel Sheet and Shapes: ASTM A240/A240M or ASTM A666, Type 304.

Steel Shapes: ASTM A36/A36M, hot-dip galvanized in accordance with ASTM A123/A123M unless otherwise indicated.

Retain three paragraphs below if requiring ladder safety railings or assist posts for roof hatches.

Steel Tube: ASTM A500/A500M, round tube.

Galvanized-Steel Tube: ASTM A500/A500M, round tube, hot-dip galvanized in accordance with ASTM A123/A123M.

Steel Pipe: ASTM A53/A53M, galvanized.

MISCELLANEOUS MATERIALS

Provide materials and types of fasteners, protective coatings, sealants, and other miscellaneous items required by manufacturer for a complete installation.

Retain one or both "Acrylic Glazing" and "Polycarbonate Glazing" paragraphs below if acrylic or polycarbonate materials are specified for glazing of hatches or heat and smoke vents. These paragraphs are two examples of common plastic-dome materials; revise to suit Project.

Acrylic Glazing: ASTM D4802, thermoformable, monolithic sheet, manufacturer's standard, Type UVA (formulated with UV absorber), Finish 1 (smooth or polished).

Polycarbonate Glazing: Thermoformable, monolithic polycarbonate sheets manufactured by extrusion process, burglar-resistance rated in accordance with UL 972 with an average impact strength of [12 to 16 ft-lbf/in. (640 to 854 J/m)] <Insert value> of width when tested in accordance with ASTM D256, Method A (Izod).

Retain one or more of first three paragraphs below, which are presented in ascending order of cost and thermal resistance.

Cellulosic-Fiber Board Insulation: ASTM C208, Type II, Grade 1, thickness as indicated.

Glass-Fiber Board Insulation: ASTM C726, nominal density of 3 lb/cu. ft. (48 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C), thickness as indicated.

Polyisocyanurate Board Insulation: ASTM C1289, thickness and thermal resistivity as indicated.

See the Evaluations in Section 061000 "Rough Carpentry" for information about waterborne preservatives.

Wood Nailers: Softwood lumber, pressure treated with waterborne preservatives for aboveground use, acceptable to authorities having jurisdiction,[ containing no arsenic or chromium,] and complying with AWPA C2; not less than 1-1/2 inches (38 mm) thick.

Retain "Security Grilles" Paragraph below if required; revise to suit Project. Security grilles are used with roof curbs, heat and smoke vents, and gravity ventilators to prevent entry through the openings. Determine bar diameter and spacing to suit Project's application and security requirements.

Security Grilles: [3/4-inch (19-mm)] <Insert dimension> diameter, ASTM A1011/A1011M steel bars spaced [6 inches (150 mm)] <Insert dimension> o.c. in one direction and [12 inches (300 mm)] <Insert dimension> o.c. in the other; factory finished as follows:

Surface Preparation: Remove mill scale and rust, if any, from uncoated steel, complying with SSPC-SP 5/NACE No. 1, "White Metal Blast Cleaning," or SSPC-SP 8, "Pickling."

Factory Priming for Field-Painted Finish: Apply shop primer specified below immediately after surface preparation and pretreatment.

Shop Primer: Manufacturer's or fabricator's standard, fast-curing, lead- and chromate-free, universal primer; selected for resistance to normal atmospheric corrosion, for compatibility with substrate and field-applied finish paint system indicated, and for capability to provide a sound foundation for field-applied topcoats under prolonged exposure.

Bituminous Coating: Cold-applied asphalt emulsion complying with ASTM D1187/D1187M.

Retain "Underlayment" Paragraph below for roof specialties applied directly over dissimilar metal or corrosive substrates.

Underlayment:

Felt: ASTM D226/D226M, Type II (No. 30), asphalt-saturated organic felt, nonperforated.

Polyethylene Sheet: 6-mil- (0.15-mm-) thick polyethylene sheet complying with ASTM D4397.

Slip Sheet: Building paper, 3 lb/100 sq. ft. (0.16 kg/sq. m) minimum, rosin sized.

Self-Adhering, High-Temperature Sheet: Minimum 30 to 40 mils (0.76 to 1.0 mm) thick, consisting of slip-resisting polyethylene-film top surface laminated to layer of butyl or SBS-modified asphalt adhesive, with release-paper backing; cold applied. Provide primer when recommended by underlayment manufacturer.

Fasteners: Roof accessory manufacturer's recommended fasteners suitable for application and metals being fastened. Match finish of exposed fasteners with finish of material being fastened. Provide nonremovable fastener heads to exterior exposed fasteners. Furnish the following unless otherwise indicated:

Fasteners for Zinc-Coated or Aluminum-Zinc Alloy-Coated Steel: Series 300 stainless steel or hot-dip zinc-coated steel in accordance with ASTM A153/A153M or ASTM F2329.

Fasteners for Aluminum Sheet: Aluminum or Series 300 stainless steel.

Fasteners for Stainless Steel Sheet: Series 300 stainless steel.

Gaskets: Manufacturer's standard tubular or fingered design of neoprene, EPDM, PVC, or silicone or a flat design of foam rubber, sponge neoprene, or cork.

Revise "Elastomeric Sealant" Paragraph below if sealant of specific type, grade, class, and use is required.

Elastomeric Sealant: ASTM C920, elastomeric [polyurethane] [silicone] polymer sealant as recommended by roof accessory manufacturer for installation indicated; low modulus; of type, grade, class, and use classifications required to seal joints and remain watertight.

Butyl Sealant: ASTM C1311, single-component, solvent-release butyl rubber sealant; polyisobutylene plasticized; heavy bodied for expansion joints with limited movement.

Asphalt Roofing Cement: ASTM D4586/D4586M, asbestos free, of consistency required for application.

GENERAL FINISH REQUIREMENTS

Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

Appearance of Finished Work: Noticeable variations in same piece are not acceptable. Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

EXECUTION

EXAMINATION

Examine substrates, areas, and conditions, with Installer present, to verify actual locations, dimensions, and other conditions affecting performance of the Work.

Verify that substrate is sound, dry, smooth, clean, sloped for drainage, and securely anchored.

Verify dimensions of roof openings for roof accessories.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Install roof accessories in accordance with manufacturer's written instructions.

Install roof accessories level; plumb; true to line and elevation; and without warping, jogs in alignment, buckling, or tool marks.

Anchor roof accessories securely in place so they are capable of resisting indicated loads.

Use fasteners, separators, sealants, and other miscellaneous items as required to complete installation of roof accessories and fit them to substrates.

Install roof accessories to resist exposure to weather without failing, rattling, leaking, or loosening of fasteners and seals.

Metal Protection: Protect metals against galvanic action by separating dissimilar metals from contact with each other or with corrosive substrates by painting contact surfaces with bituminous coating or by other permanent separation as recommended by manufacturer.

Coat concealed side of [uncoated aluminum] [stainless steel] roof accessories with bituminous coating where in contact with wood, ferrous metal, or cementitious construction.

Underlayment: Where installing roof accessories directly on cementitious or wood substrates, install a course of underlayment and cover with manufacturer's recommended slip sheet.

Bed flanges in thick coat of asphalt roofing cement where required by manufacturers of roof accessories for waterproof performance.

Roof Curb Installation: Install each roof curb so top surface is level.

Equipment Support Installation: Install equipment supports so top surfaces are level with each other.

Roof-Hatch Installation:

Verify that roof hatch operates properly. Clean, lubricate, and adjust operating mechanism and hardware.

Attach safety railing system to roof-hatch curb.

Attach ladder-assist post in accordance with manufacturer's written instructions.

Heat and Smoke Vent Installation:

Install heat and smoke vent so top perimeter surfaces are level.

Install and test heat and smoke vents and their components for proper operation in accordance with NFPA 204.

Gravity Ventilator Installation: Verify that gravity ventilators operate properly and have unrestricted airflow. Clean, lubricate, and adjust operating mechanisms.

Pipe Support Installation: Comply with MSS SP-58 and MSS SP-89. Install supports and attachments as required to properly support piping. Arrange for grouping of parallel runs of horizontal piping, and support together.

Pipes of Various Sizes: Space supports for smallest pipe size or install intermediate supports for smaller diameter pipes as specified for individual pipe hangers.

Preformed Flashing-Sleeve[ and Flashing Pipe Portal] Installation: Secure flashing sleeve to roof membrane in accordance with flashing-sleeve manufacturer's written instructions; flash sleeve flange to surrounding roof membrane in accordance with roof membrane manufacturer's instructions.

Retain "Security Grilles" Paragraph below for field-installed security grilles. Retain option if ends of bars cannot be welded to structural frame or curb walls.

Security Grilles: Weld bar intersections and[, using tamper-resistant bolts, attach the] ends of bars to structural frame or primary curb walls.

Roof Walkway Installation:

Verify that locations of access and servicing points for roof-mounted equipment are served by locations of roof walkways.

Retain first subparagraph below for ballasted low-slope roofing.

Remove ballast from top surface of low-slope roofing at locations of contact with roof-walkway supports.

Install roof walkway support pads prior to placement of roof walkway support stands onto low-slope roofing.

Redistribute removed ballast after installation of support pads.

Seal joints with [elastomeric] [or] [butyl] sealant as required by roof accessory manufacturer.

REPAIR AND CLEANING

Retain "Galvanized Surfaces" Paragraph below for galvanized-steel surfaces.

Galvanized Surfaces: Clean field welds, bolted connections, and abraded areas and repair galvanizing in accordance with ASTM A780/A780M.

Retain first paragraph below for primed surfaces.

Touch up factory-primed surfaces with compatible primer ready for field painting in accordance with Section 099113 "Exterior Painting."

Clean exposed surfaces in accordance with manufacturer's written instructions.

Clean off excess sealants.

Replace roof accessories that have been damaged or that cannot be successfully repaired by finish touchup or similar minor repair procedures.

END OF SECTION 077200